Broken roof tile.

Photograph 59

Broken roof tile and roof undulations approximately over roof leak.

Photograph 60

Cracked and moving site / garden wall.

Photograph 61

Cracked and moving site / garden wall.

Photograph 62 Evidence of roof leak.

Photograph 64 Clubhouse Building

Gang-nail plate pulled off truss members.

Photograph 65

Damage wood roof truss. Gang-nail plate has been pulled off truss members.

Altered wood roof truss. Web elements removed.

Photograph 66

Altered wood roof trusses. Web elements have been removed with no apparent modification to truss design.

Altered wood roof trusses. Web elements removed.

Photograph 67

Additional altered wood roof trusses. Web elements removed with out any apparent truss modification.

Girder truss end. Required tie down not provided.

Photograph 68

Girder roof truss bearing without tie down to support.

Water damage.

Photograph 69

Water damage to roof sheathing, fascia, soffit, and truss end. Water intrusion occurred at end of internal roof gutter system.

Added plywood gussets plates.

Photograph 70

Altered wood roof truss. Plywood gussets plates have been added to truss panel points in an attempt to restore panel point connection. It is unclear why gussets plates were added or if repair is adequate.

Point of fracture.

Photograph 71

Material facture at end bearing of girder roof truss. It is unclear why or when fracture occurred. Additional investigation is recommended.

Point of fracture.

Photograph 72

Side view of girder truss fracture.

Wood damage.

Gutter splice location.

Photograph 73
Water damage to facia and soffit framing due to leak in internal roof gutter at gutter splice location.

Photograph 74

Water damage to truss tail, soffit and fascia framing. Damage has occurred at end of internal roof gutter system.

Damaged roof truss gang-nail plate.

Photograph 75

Damaged roof truss gang-nail plates.

Cracked fascia stucco finish.

Photograph 76

Cracked stucco finish on fascia, directly forward of internal roof gutter system.

Missing snap covers for storefront.

Photograph 77

Missing snap cover for storefront.

Photograph 78

Heavily cracked and delaminated stucco finish on exterior building wall.

Photograph 79

Heavily cracked and delaminated stucco finish on exterior building wall. Copper staining on wall from leak in copper roof gutter.

Weep holes.

No weep holes.

Photograph 80

Added weep holes in storefront windows.

Photograph 81

Facilities Maintenance
.

Photograph 82

Wood damage to roof sheathing and fascia.

Photograph 83

Water damage to entry door.

Photograph 84 Agricultural Barn Building.

Photograph 85

Missing gutter down spout causing erosion and undermining concrete slab and asphalt.

Steel base angle.

Steel jamb column.

Photograph 86

Cold form steel jamb column at side of garage door and steel base angel, both which provide lateral load resistance, (wind), have completely corroded through.

Rigid frame steel column.

Steel jamb column.

Steel base angle.

Photograph 87

Steel base angle and cold form steel jamb column, which provides lateral resistance for wall panel have completely corroded through. Base of steel rigid frame is also experiencing active corrosion.